## Soils
Narromine Shire Council
Narromine Sewage Treatment Plant
EPL No. 11715
Link to EPL register: | https://apps.epa.nsw.gov.au/prpoeoapp/ViewPOEOLicence.aspx?DOCID=152632&SYSUID=1&LICID=11715
[8 empty] | Inorganics | Inorganics | Inorganics | Exchangeable cations | Exchangeable cations | Exchangeable cations | Nutrients | Nutrients
[8 empty] | pH (Lab) | Electrical Conductivity (Saturated Paste) | Sodium Adsorption Ratio | Exchangeable Calcium | Exchangeable Magnesium | Exchangeable Sodium | Nitrogen (Total) | Phosphorus (Total)
[8 empty] | pH units | µS/cm | - | meq/100g | meq/100g | meq/100g | mg/kg | mg/kg
Detection limit | [7 empty] | 0.1 | 1 | 0.01 | 0.1 | 0.1 | 0.1 | 20 | 2
EPA ID Point | Location Code | Date / Time | Time | Results Received | Results Published | Depth (m) | Name of Sampler
EPA ID Point 7 | SS1 | 2018-06-19 | 10:28 | 2018-06-25 | 2018-07-01 | 0 - 0.1 | Bill Foster | 6.1 | - | - | 3.6 | 1.1 | 0.3 | 890 | 186
|  | 2019-05-21 | 8:05 | 2019-05-30 | 2019-06-07 | 0 - 0.15 | Bill Foster | 5.9 | 218 | 1.16 | 3.4 | 1.4 | 0.1 | 720 | 184
|  | 2020-05-12 | 15:00 | 2020-05-25 | 2020-06-01 | 0 - 0.1 | Grace Rogers | 6.6 | 256 | 2.07 | 3.5 | 1 | 0.3 | 670 | 213
|  | 2021-05-25 | 11:30 | 2021-05-26 | 2021-06-05 | 0 - 0.1 | Grace Rogers | 6.7 | 192 | 4.33 | 0.31 | 1.1 | 0.3 | 880 | 228
|  | 2021-05-25 | 11:30 | 2021-05-26 | 2021-06-05 | 0.6 | Grace Rogers | 6.4 | 241 | 6.52 | 3.8 | 2.3 | 0.5 | 220 | 108
|  | 2021-05-25 | 11:30 | 2021-05-26 | 2021-06-05 | 1 | Grace Rogers | 6.4 | 653 | 7.01 | 6.2 | 7.2 | 0.8 | 240 | 116
| SS2 | 2018-06-19 | 15:00 | 2018-06-25 | 2018-07-01 | 0 - 0.1 | Bill Foster | 6.8 | - | - | 6.3 | 2.2 | 0.9 | 940 | 226
|  | 2019-05-21 | 7:50 | 2019-05-30 | 2019-06-07 | 0 - 0.15 | Bill Foster | 6.4 | 584 | 3.87 | 5.3 | 2.1 | <0.1 | 1200 | 267
|  | 2020-05-12 | 15:00 | 2020-05-25 | 2020-06-01 | 0 - 0.1 | Grace Rogers | 6.8 | 691 | 4.6 | 5 | 2.4 | 1 | 740 | 230
|  | 2021-05-25 | 12:00 | 2021-05-26 | 2021-06-05 | 0 - 0.1 | Grace Rogers | 7.1 | 193 | 3.41 | 4.9 | 2.3 | 0.5 | 470 | 127
|  | 2021-05-25 | 12:00 | 2021-05-26 | 2021-06-05 | 0.6 | Grace Rogers | 7.2 | 594 | 7.08 | 3.6 | 2.5 | 0.6 | 230 | 117
|  | 2021-05-25 | 12:00 | 2021-05-26 | 2021-06-05 | 1 | Grace Rogers | 7.4 | 891 | 3.69 | 4.4 | 4 | 0.3 | 340 | 164

## Effluent
Narromine Shire Council
Narromine Sewage Treatment Plant
EPL No. 11715
Link to EPL register: | https://apps.epa.nsw.gov.au/prpoeoapp/ViewPOEOLicence.aspx?DOCID=152632&SYSUID=1&LICID=11715
[5 empty] | Inorganics | Inorganics | Inorganics | Inorganics | Nutrients | Nutrients | Nutrients | Nutrients | Organic Indicators | TPH
[5 empty] | pH (Lab) | Electrical conductivity (lab) | Total Suspended Solids | Sodium Adsorption Ratio (filtered) | Nitrogen (Total Oxidised) (as N) | Nitrogen (Total) | Kjeldahl Nitrogen Total | Phosphorus (Total) | BOD | Oil & Grease
[5 empty] | pH Units | µS/cm | mg/L | - | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
Detection Limit |  |  |  |  | 0.01 | 1 | 1 | 0.01 | 0.01 | 0.1 | 0.1 | 0.01 | 2 | 5
Location Code | Sample Date and Time | Samples Received | Results Published | Name of Sampler | pH (Lab) | Electrical conductivity (lab) | Total Suspended Solids | Sodium Adsorption Ratio (filtered) | Nitrogen (Total Oxidised) (as N) | Nitrogen (Total) | Kjeldahl Nitrogen Total | Phosphorus (Total) | BOD | Oil & Grease
EPA Point 5 | 2016-01-22 15:00 | 2016-01-22 | 2016-01-29 | Ben Morrison | 9.39 | 1300 | 82 | 6.83 | 0.03 | 9.6 | 9.6 | 1.96 | <2 | <5
EPA Point 5 | 2016-02-29 15:00 | 2016-03-01 | 2016-03-07 | Ben Morrison | 9.7 | 1410 | 62 | 7.39 | 0.05 | 9.2 | 9.1 | 1.46 | 7 | 30
EPA Point 5 | 2016-04-18 12:30 | 2016-04-21 | 2016-04-28 | James Walsh | 8.57 | 1420 | 64 | 7.41 | 0.52 | 13.2 | 12.7 | 4.08 | 40 | <5
EPA Point 5 | 2016-05-24 10:45 | 2016-05-26 | 2020-06-02 | Anthony Everett | 8.52 | 1300 | 44 | 5.63 | 1.43 | 8.9 | 7.5 | 4.55 | 30 | <5
EPA Point 5 | 2016-07-26 15:00 | 2016-07-27 | 2016-08-03 | Paul McDougall | 8.01 | 1020 | 81 | 4.66 | 3.35 | 13 | 9.6 | 4.87 | 27 | 6
EPA Point 5 | 2016-08-30 12:00 | 2016-08-31 | 2016-09-05 | Anthony Everett | 7.88 | 1120 | 26 | 4.72 | 0.3 | 12.9 | 12.6 | 5.87 | 6 | <5
EPA Point 5 | 2016-10-06 09:00 | 2016-10-07 | 2016-10-13 | Ben Morrison | 7.83 | 1020 | 36 | 4.53 | 9.02 | 16.7 | 7.7 | 4.89 | 27 | 12
EPA Point 5 | 2016-11-21 09:45 | 2016-11-24 | 2016-12-01 | Ben Morrison | 7.79 | 1070 | 118 | 5.48 | 0.06 | 14.5 | 14.4 | 5.78 | 9 | <5
EPA Point 5 | 2016-12-15 15:00 | 2016-12-16 | 2016-12-29 | Paul McDougall | 8.69 | 1220 | * | 5.83 | 0.14 | 1.3 | 1.2 | 0.05 | 25 | <5
EPA Point 5 | 2017-02-02 15:00 | 2017-02-03 | 2017-02-10 | Ben Morrison | 8.68 | 1440 | 145 | 5.7 | <0.01 | 17.2 | 17.2 | 2.74 | 29 | <5
EPA Point 5 | 2017-03-13 15:00 | 2017-03-14 | 2017-03-21 | Ben Morrison | 8.25 | 1660 | 127 | 9 | 0.05 | 12.6 | 12.6 | 3.4 | 84 | <5
EPA Point 5 | 2017-04-27 16:36 | 2017-04-28 | 2017-05-05 | Ben Morrison | 8.17 | 1490 | 68 | 6.01 | 1.32 | 10.1 | 8.8 | 4.43 | 29 | <5
EPA Point 5 | 2017-06-08 10:50 | 2017-06-09 | 2017-07-04 | Paul McDougall | 8.92 | 1360 | 75 | 5.43 | 1.39 | 9.3 | 7.9 | 3.63 | 26 | <5
EPA Point 5 | 2017-07-27 15:00 | 2017-07-28 | 2017-08-04 | James Walsh | 7.69 | 1300 | 82 | 5.3 | 4.37 | 17 | 12.6 | 5.16 | 47 | <5
EPA Point 5 | 2017-11-08 12:00 | 2017-11-09 | 2017-11-16 | Geoff Metcalfe | 7.94 | 1310 | 30 | 5.96 | 1.13 | 9.5 | 8.4 | 4.19 | 7 | <5
EPA Point 5 | 2017-12-20 15:00 | 2017-12-21 | 2018-01-04 | Paul McDougall | 8.87 | 1310 | 124 | 6.04 | <0.01 | 10.4 | 10.4 | 5.08 | 43 | <5
EPA Point 5 | 2018-03-12 12:00 | 2018-03-13 | 2018-03-20 | Duane Donnelly | 9.16 | 1680 | 100 | 6.81 | 0.02 | 8.5 | 8.5 | 2.57 | 20 | <5
EPA Point 5 | 2018-04-11 14:17 | 2018-04-12 | 2018-04-19 | Geoff Metcalfe | 8.68 | 1850 | 93 | 7.4 | 0.06 | 13.1 | 13 | 3.55 | 44 | <5
EPA Point 5 | 2018-04-24 15:00 | 2018-04-24 | 2018-05-02 | Duane Donnelly | 8.65 | 1860 | 116 | 6.56 | 0.86 | 18.7 | 17.8 | 5.53 | 50 | 5
EPA Point 5 | 2018-06-04 12:00 | 2018-06-05 | 2018-06-12 | Anthony Everett | 8.64 | 1720 | 102 | 6.45 | 1.83 | 11.5 | 9.7 | 4.79 | 62 | 9
EPA Point 5 | 2018-07-16 11:35 | 2018-07-17 | 2018-07-23 | Anthony Everett | 8.83 | 1480 | 76 | 5.34 | 3.18 | 16.4 | 13.2 | 5.8 | 58 | <5
EPA Point 5 | 2018-08-27 11:00 | 2018-08-28 | 2018-09-03 | Anthony Everett | 8.96 | 1340 | 135 | 5.11 | 5.2 | 23.6 | 18.4 | 4.4 | 42 | <5
EPA Point 5 | 2018-10-08 11:00 | 2018-10-09 | 2018-10-15 | Anthony Everett | 8.63 | 1430 | 82 | 4.99 | 2.64 | 14.5 | 11.9 | 6.5 | 32 | <5
EPA Point 5 | 2018-11-19 15:00 | 2018-11-20 | 2018-11-27 | Anthony Everett | 8.68 | 1480 | 105 | 5.53 | 0.6 | 7.8 | 7.2 | 4.34 | 45 | <5
EPA Point 5 | 2019-02-11 15:00 | 2019-02-12 | 2019-02-19 | Anthony Everett | 8.42 | 1680 | 90 | 5.72 | <0.01 | 10.4 | 10.4 | 4.36 | 59 | <5
EPA Point 5 | 2019-05-21 06:40 | 2019-05-22 | 2019-05-30 | Bill Foster | 8.01 | 1630 | 84 | 5.5 | 3.31 | 13.1 | 9.8 | 5.84 | 46 | <5
EPA Point 5 | 2019-08-21 17:30 | 2019-08-23 | 2019-08-29 | Bill Foster | 7.72 | 1510 | 57 | 5.76 | 2.59 | 17.8 | 15.2 | 5.64 | 209 | <5
EPA Point 5 | 2019-12-03 15:15 | 2019-12-05 | 2019-12-13 | Bill Foster | 8.08 | 1610 | 69 | 6.73 | 0.12 | 6.8 | 6.7 | 3.15 | 45 | <5
EPA Point 5 | 2020-02-25 09:15 | 2020-02-28 | 2020-03-06 | Bill Foster | 7.01 | 2020 | 120 | 7.25 | 0.74 | 11.7 | 11 | 3.34 | 43 | <5
EPA Point 5 | 2020-05-12 10:25 | 2020-05-14 | 2020-05-25 | Grace Rogers | 8.54 | 1130 | 88 | 4.87 | 0.77 | 10.9 | 10.1 | 4.71 | 20 | 5
EPA Point 5 | 2020-06-09 | 2020-06-10 | 2020-06-17 | Kyle Whalan | 8.42 | 1170 | 88 | 3.7 | 0.37 | 11.1 | 10.7 | 6.17 | 26 | <5
EPA Point 5 | 2020-08-18 | 2020-08-21 | 2020-08-28 | Grace Rogers | 7.92 | 930 | 72 | 4.29 | 5.33 | 14.4 | 9.1 | 4.32 | 40 | 5
EPA Point 5 | 2020-11-10 10:10 | 2020-11-20 | 2020-11-27 | Grace Rogers | 8.4 | 1190 | 114 | 4.69 | 0.11 | 15.6 | 15.5 | 5.88 | 35 | 13
EPA Point 5 | 2021-02-02 10:27 | 2021-02-05 | 2021-02-12 | Grace Rogers | 8.15 | 1360 | 163 | 5.7 | 0.56 | 15.3 | 14.7 | 3.39 | 56 | <5
EPA Point 5 | 2021-05-26 | 2021-05-26 | 2021-06-05 | Grace Rogers | 8.46 | 1160 | 103 | 4.77 | 2.77 | 12.4 | 9.6 | 4.22 | 27 | <5
EPA Point 5 | 2021-08-30 | 2021-08-31 | 2021-09-08 | Anthony Everett | 7.67 | 1080 | 22 | 4.54 | 2.83 | 16.6 | 13.8 | 5.5 | 17 | <5
EPA Point 5 | 2021-12-09 15:00 | 2021-12-14 | 2021-12-22 | Grace Rogers | 8.26 | 1070 | 63 | 4.75 | 0.16 | 7 | 6.8 | 3.65 | 13 | 7
EPA Point 5 | 2022-02-21 | 2022-02-23 | 2022-03-07 | Grace Rogers | 8.24 | 1250 | 143 | 5.46 | 0.09 | 19.9 | 19.8 | 5.46 | 21 | <5
* A Total Suspended Solids sample (TSS) was not obtained at EPA point 5 on 15/12/2016 due to the parameter not being specified to the laboratory on the chain of custody form.
At the time of sampling, TSS was required to be monitored six times per reporting period as per EPL 11715 (Licence version date 16/06/2014), a total of eight TSS samples were collected during the 2015-2016 reporting period.
This was displayed in the 2016 Annual Return and was not a non-compliance.